## CETP MECH TECHNICAL
Appendix 3 - Annex B - Mechanical Technical Form
UNIDO Common Effluent Treatment Plant (CETP) in Sialkot Tannery Zone; Pakistan
| UNIDO ITB No. |  |  |  | Date:
Project: Mechanical and Electrical works, delivery and installation of process equipment, commissioning, training and trial operation.
TECHNICAL EVALUATION OF OFFERS FOR CETP WILL BE BASED ON THIS FORM
1. Mechanical Work
LOT 1 – SUPPLY OF MECHANICAL COARSE SCREENS
S.No. | Item Description | Unit | Quantity | OFFERED ITEM MEETS OR EXCEEDS THE SAMPLE TECHNICAL SPECIFICATIONS - Y/N | OFFERED MODEL (exact brand and model name etc.) | Remark (brochure, details, web link)
1 | Supplyof Mechanical Coarse Screens (MCS01/01-02)for Beam House effluent, including all accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 2
2 | Supplyof Mechanical Coarse Screens (MCS02/01-02) for Tan House effluent, including, all accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 2
3 | Supplyof Screen Washer (SW01/01-04) for beam hosue and tan house screenings, including all accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 4
4 | Supply of FRP Container 1.1 m3(FC03/01-04) for Tan House and Beam House screening, two each respectively, including, allaccessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 4
5 | The Supplier must provide a final report (in English) should be submitted to UNIDO no later than 2 weeks after the delivery and installation of serial number 1 to 4 equipment have been completed. | No | 4
6 | The supplier must carry out trainings of serial number 1 and 3 equipment for the duration as per the requirements of the specific equipment on the installation site of the procure equipment and is aimed at equipping the national expertise with necessary skills and knowledge for maintenance of machines and equipment being procured and operation to produce various building components | No | 2
Technical Specifications (MCS01)
| Clear spacing b/w bars |  | 15 mm | Screen Chamber width |  | 600 mm
| Height of Screen |  | 1500 mm | Approach velocity and Flow |  | 0.65 m/sec and 95 liters/sec
| Screen angle with horizontal |  | 60° | Water depth |  | 300 mm
| Material |  | Stainless Steel 316 | Medium |  | Tannery Wastewater
Technical Specifications (MCS02)
| Clear spacing b/w bars |  | 15 mm | Screen Chamber width |  | 1000 mm
| Height of Screen |  | 1500 mm | Approach velocity and Flow |  | 0.65 m/sec and 160 liters/sec
| Screen angle with horizontal |  | 60° | Water depth |  | 300 mm
| Material |  | Stainless Steel 316 | Medium |  | Tannery Wastewater
Technical Specifications (FC03)
| Container Material | FRP with vinyl ester resin |  |  | Exposed Metal | ANSI Type 316 stainless steel
| Capacity | 1.1 m3 |  |  | Protected Metal | ASTM A36, with fiberglass reinforced plastic coating
Technical Specifications (SW01)
| Max. Throughput |  | 2.2 m3/hr | Optimized Output |  | 1.3 m3/hr
| Min. Organics Output |  | 1.1 m3/hr | 6mm Screen Water Capacity |  | 15.8 l/sec
Screen washer including: Grinder Motor, Compaction Screw Motor, Programmable Washing Cycle, Dedicated Wash Zone, Tank Flush, Compaction Elbow Flush, and Motion Compaction-Sensor Screw,
Drawing Number: M-0119 & M-0121
LOT 2 – SUPPLY OF VORTEX GRIT CHAMBER
S.No. | Item Description | Unit | Quantity | OFFERED ITEM MEETS OR EXCEEDS THE SAMPLE TECHNICAL SPECIFICATIONS - Y/N | OFFERED MODEL (exact brand and model name etc.) | Remark (brochure, details, web link)
1 | Supply of Vortex Grit Chamber with Classifier (GC01/01-02) for Beam House effluent, including all piping and other accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 2
2 | Supply of Vortex Grit Chamber with Classifier (GC02/01-02) for Tan House effluent, including, all piping and other accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 2
3 | Supply of FRP Container 5 m3(FC01/01-05) for Tan House and Beam House wastewatergrit, including, allaccessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 5
4 | Supply of Fork Lifter (FL01/01-02) for all type of lifting of containers either chemical or others, including, allaccessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 2
5 | The Supplier must provide a final report (in English) should be submitted to UNIDO no later than 2 weeks after the delivery and installation of serial number 1 to 4 equipment have been completed. | No | 4
6 | The supplier must carry out trainings of serial number 1 and 4 equipment for the duration as per the requirements of the specific equipment on the installation site of the procure equipment and is aimed at equipping the national expertise with necessary skills and knowledge for maintenance of machines and equipment being procured and operation to produce various building components | No | 2
Technical Specifications (GC01)
| Medium |  | Beam House Wastewater | Max overflow rate and Flow | 0.030 m3/m2/sec and 95 liters/sec
| HRT |  | 60 seconds | Mechanism | Automatic Grit Removal Mechanism
Technical Specifications (GC02)
| Medium | Tanning and Post TannnigWastewater |  | Max overflow rate and Flow | 0.0314 m3/m2/sec and 160 liters/sec
| HRT | 60 seconds |  | Mechanism | Automatic Grit Removal Mechanism
Technical Specifications (FC01)
| Container Material | FRP with vinyl ester resin |  | Exposed Metal | ANSI Type 316 stainless steel
| Capacity | 5 m3 |  | Protected Metal | ASTM A36, with fiberglass reinforced plastic coating
Technical Specifications (FL01)
| Load capacity | 7000 kg |  | Engine Power | 75kW (102 ps) @ 2,200 rm
| Lifting speed unloaded | 460 / 460 / 480 mm/s |  | Travel speed unloaded | 33.9 / 33.6 / 35 km/h
Drawing Number: M-0112 & M-0113
LOT 3 – SUPPLY OF OIL AND GREASE SEPARATOR
S.No. | Item Description | Unit | Quantity | OFFERED ITEM MEETS OR EXCEEDS THE SAMPLE TECHNICAL SPECIFICATIONS - Y/N | OFFERED MODEL (exact brand and model name etc.) | Remark (brochure, details, web link)
1 | Supply of Oil & Grease Separator (OGS01/01-02) for Beam House effluent, including all piping and other accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 2
2 | Supply of Oil & Grease Separator (OGS01/01-02) for Tan House effluent, including, all piping and other accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 2
3 | Supply of FRP Container 2 m3(FC02/01-02) for Tan House and Beam House wastewaterwaste oil, including, allaccessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 2
4 | The Supplier must provide a final report (in English) should be submitted to UNIDO no later than 2 weeks after the delivery and installation of serial number 1 to 3 equipment have been completed. | No | 3
5 | The supplier must carry out trainings of serial number 1 equipment for the duration as per the requirements of the specific equipment on the installation site of the procure equipment and is aimed at equipping the national expertise with necessary skills and knowledge for maintenance of machines and equipment being procured and operation to produce various building components | No | 1
Technical Specifications (OGS01)
| Medium | Tannery Wastewater |  | Max overflow rate | 95 liters/sec
| Mechanism | Automatic Oil & Grease Removal Mechanism with waste oil submerssible pump
Technical Specifications (OGS02)
| Medium | Tannery Wastewater |  | Max overflow rate | 160 liters /sec
| Mechanism | Automatic Oil & Grease Removal Mechanism with waste oil submerssible pump
Technical Specifications (FC02)
| Container Material |  | FRP with vinyl ester resin | Exposed Metal | ANSI Type 316 stainless steel
| Capacity |  | 2 m3 | Protected Metal | ASTM A36, with fiberglass reinforced plastic coating
Drawing Number: M-0110
LOT 4 – SUPPLY OF WASTEWATER PUMPS
S.No. | Item Description | Unit | Quantity | OFFERED ITEM MEETS OR EXCEEDS THE SAMPLE TECHNICAL SPECIFICATIONS - Y/N | OFFERED MODEL (exact brand and model name etc.) | Remark (brochure, details, web link)
1 | Supply of Wastewater Pump (WPS) (WSP01/01-02) in Wastewater Pumping Station (WPS) for Beam House effluent, including all piping and other accessoriesrequired inside pumping stationfor installation and operation, complete in all respects, in accordance with the contract documents. | No | 2
2 | Supply of Wastewater Pump (WSP) (WSP02/01-02) in Wastewater Pumping Station (WPS) for Tanning and Post tanning effluent, including, all piping and other accessories required inside pumping station for installation and operation, complete in all respects, in accordance with the contract documents. | No | 2
3 | Supply of Submersible Sump Pumps (Bilge Pump SBP01/01-08)1+1 standby in each Wastewater Pumping Station (WPS) and 1+1 standby in each sludge pumping rooms,including pump-motor set, pump base, anchor bolts, painting/coatings and other accessories, complete in all respects, in accordance with the contract documents. | No | 8
4 | Supply of Gantry Crane (GC01/01) in each Wastewater Pumping Station (WPS) including all accessories, complete in all respects, in accordance with the contract documents. | No | 1
5 | The Supplier must provide a final report (in English) should be submitted to UNIDO no later than 2 weeks after the delivery and installation of serial number 1 to 4 equipment have been completed. | No | 3
6 | The supplier must carry out trainings of serial number 1 and 4 equipment for the duration as per the requirements of the specific equipment on the installation site of the procure equipment and is aimed at equipping the national expertise with necessary skills and knowledge for maintenance of machines and equipment being procured and operation to produce various building components | No | 2
Technical Specifications (WSP01)
| Medium | Tannery Wastewater | Pump Type | Heavy-duty (horizontal, direct-coupled /vertical, pedestal mounted dry- pit), single-suction, centrifugal, CW rotation, Centrifugal
| Capacity | 70 m3/h | Head | 09 m
| Free Pass | 80 – 100 mm | Efficiency | Guaranteed Duty Point (GDP) is between 80% and 120% of the flow rate at the Best Efficiency Point (BEP).
| Pump Casing | Cast Iron and shall comply with BS EN 1563 / EN-GJS-700-2 | Casing Wear Ring | Cast S.G. Iron and shall comply with BS EN 1563 / EN-GJS-450-10
| Impeller | Cast S.G. Iron and shall comply with BS EN 1563 / EN-GJS-700-2 | Phase/Voltage | 3/400 V
| Frequency | 50 Hz | Efficiency | Motor efficiency shall comply with the requirements of IEC 60034 - 30 high efficiency Class IE2.
| IP | 55 | Insulation Class | F
Technical Specifications (WSP02)
| Medium | Tannery Wastewater | Pump Type | Heavy-duty (horizontal, direct-coupled /vertical, pedestal mounted dry- pit), single-suction, centrifugal, CW rotation, Centrifugal
| Capacity | 110 m3/h | Head | 09 m
| Free Pass | 80 – 100 mm | Efficiency | Guaranteed Duty Point (GDP) is between 80% and 120% of the flow rate at the Best Efficiency Point (BEP).
| Pump Casing | Cast Iron and shall comply with BS EN 1563 / EN-GJS-700-2 | Casing Wear Ring | Cast S.G. Iron and shall comply with BS EN 1563 / EN-GJS-450-10
| Impeller | Cast S.G. Iron and shall comply with BS EN 1563 / EN-GJS-700-2 | Phase/Voltage | 3/400 V
| Frequency | 50 Hz | Efficiency | Motor efficiency shall comply with the requirements of IEC 60034 - 30 high efficiency Class IE2.
| IP | 55 | Insulation Class | F
Technical Specifications (SBP01)
| Medium | Tannery Wastewater | Pump Type | Single stage centrifugal type having radial or mixed flow impellers and shall be suitable for continuous running under complete or partially submerged conditions.
| Capacity | 15 m3/h | Head | 10 m
| Efficiency | * | Pump Casing | High cast iron (fine grained meehanite) free from blow-holes or imperfections, of ample proportions throughout, with all internal passages finished smooth. |  | * Guaranteed Duty Point (GDP) is between 80% and 120% of the flow rate at the Best Efficiency Point (BEP).
| Impeller | * | Phase/Voltage | 3/400 V |  | * High-grade cast iron shall be keyed to the shaft and secured by locking screws. Single or double shrouded, statically and dynamically balanced, with interchangeable bearings and a ball clearance of at least 100 mm, non clogging type. Back vanes shall be provided on the discharge side shroud to minimize the ingress of abrasive matter to the shaft seal.
| Frequency | 50 Hz | Efficiency | Suitable for operating below water level, protection class IP 68 (IEC 34.5/144) isolation class B (IEC 85), shall be provided with windings for 3 x 400 V-50 Hz.
| IPand Insulation Class | 68 and F | Location | Wastewater pumping station and all three sludge pumping rooms.
Technical Specifications (GC01)
| Type | Double Girder Gantry (overhead) Crane
| Capacity | 0.5 tons | Hoisting Unit | Capable of lifting 10 m free C-type hook travel with latch, hoist shall be designed and manufactured in accordance with B.S 466 (1984) and B.S 2573 (1980) for indoor duty.
| Bay Length and Span | 9.0 m and 6.6 m | Travel Motors | Travel motors shall be rated 60% E.D with IP 55 protection, “Insulation class F” and soft starting inertia flywheels plus soft stopping adjustable torque brakes giving the operator excellent control throughout the load spectrum.
Drawing Number: M-0122
LOT 5 – SUPPLY OF JET AERATORS
S.No. | Item Description | Unit | Quantity | OFFERED ITEM MEETS OR EXCEEDS THE SAMPLE TECHNICAL SPECIFICATIONS - Y/N | OFFERED MODEL (exact brand and model name etc.) | Remark (brochure, details, web link)
1 | Supply of Jet Aerators Submersible Ejector shaft type (JA01/01-02) in Equalization tank for Beam House effluent, including all accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 2
2 | Supply of Aerators Submersible Ejector shaft type (JA02/01-02)in Equalization tank for Tanning & Post Tanning effluent, including, all accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 2
3 | The Supplier must provide a final report (in English) should be submitted to UNIDO no later than 2 weeks after the delivery and installation of serial number 1 to 2 equipment have been completed. | No | 2
4 | The supplier must carry out trainings of serial number 1 equipment for the duration as per the requirements of the specific equipment on the installation site of the procure equipment and is aimed at equipping the national expertise with necessary skills and knowledge for maintenance of machines and equipment being procured and operation to produce various building components | No | 1
Technical Specifications (JA01)
| Medium | Tannery Wastewater | Type | Submersible Ejector Shaft with lifting arrangement
| Air Discharge (each) | 18 Nm3/min | Pumping Head | 4.0 m
Technical Specifications (JA02)
| Medium | Tanning and Post Tanning Effluent | Type | Submersible Ejector Shaft with lifting arrangement
| Air Discharge (each) | 30 Nm3/min | Pumping Head | 4.0 m
Drawing Number: M-0111
LOT 6 – SUPPLY OF TURBINE AND PADDLE MIXERS
S.No. | Item Description | Unit | Quantity | OFFERED ITEM MEETS OR EXCEEDS THE SAMPLE TECHNICAL SPECIFICATIONS - Y/N | OFFERED MODEL (exact brand and model name etc.) | Remark (brochure, details, web link)
1 | Supply of Mixer (MRMT01/01) for Rapid Mixing Tank, including MS Walkway and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 1
2 | Supply of Mixer (MFT01/01) for Flocculation Tank, including MS Walkway and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 1
3 | Supply of Mixer (MPT01/01-02) for Pre-Selector Tank, including MS Walkway and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 2
4 | Supply of Mixer (MCOT01/01) for Chemical Oxidation Tank, including MS Walkway and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 1
5 | Supply of Mixer (MCDT01/01-04) for Chemical Dosing Tanks, including all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 8
6 | The Supplier must provide a final report (in English) should be submitted to UNIDO no later than 2 weeks after the delivery and installation of serial number 1 to 5 equipment have been completed. | No | 5
7 | The supplier must carry out trainings of serial number 1 to 5 equipment for the duration as per the requirements of the specific equipment on the installation site of the procure equipment and is aimed at equipping the national expertise with necessary skills and knowledge for maintenance of machines and equipment being procured and operation to produce various building components | No | 5
Technical Specifications (MRMT01)
| Medium | Tannery Wastewater | Type | Turbine Propeller Mixers
| Tank Length | 1700 mm | Tank Width | 1700 mm
| Tank Water Depth | 1250 mm | Agitator type | Top Entry, Turbine 6 Blades with 45˚ with Agitator Shaft
| Material (Shaft & Propeller) | SS 316L | Material (Flange, Nuts & Bolts) | SS 316L
| Phase/Voltage | 3/400 V | Frequency | 50 Hz
| Velocity gradient | 1500/sec | IP | 65
| Insulation Class | F
Technical Specifications (MFT01)
| Medium | Tannery Wastewater | Type | Paddle Mixers
| Tank Length | 5400 mm | Tank Width | 5400 mm
| Tank Water Depth | 3000 mm | Agitator type | Top Entry, Paddle Type
| Material (Shaft & Propeller) | SS 316L | Material (Flange, Nuts & Bolts) | SS 316L
| Phase/Voltage | 3/400 V | Frequency | 50 Hz
| Speed of rotation (output) | 10-15 rpm | IP | 65
| Insulation Class | F
Technical Specifications (MPT01)
| Medium | Tannery Wastewater | Type | Turbine Propeller Mixers
| Tank Length | 4000 mm | Tank Width | 4000 mm
| Tank Water Depth | 4000 mm | Agitator type | Top Entry, Turbine 6 Blades with 45˚ with Agitator Shaft
| Material (Shaft & Propeller) | SS 316L | Material (Flange, Nuts & Bolts) | SS 316L
| Phase/Voltage | 3/400 V | Frequency | 50 Hz
| Speed of rotation (output) | 50 rpm | IP | 65
| Insulation Class | F
Technical Specifications (MCOT01)
| Medium | Tannery Wastewater | Type | Turbine 6 Flat Blades, Vain Disk
| Diameter | 7000 mm | Tank Water Depth | 3000 mm
| Material (Shaft & Propeller) | SS 316L | Agitator type | Top Entry, Turbine 6 Blades with 45˚ with Agitator Shaft
| Material (Flange, Nuts & Bolts) | SS 316L | Phase/Voltage | 3/400 V
| Velocity gradient | 100/sec | Frequency | 50 Hz
| Insulation Class | F | IP | 65
Technical Specifications (MCDT01)
| Medium | MnSO4, Alum, K-Polymer, HCl (2 mixers), NaOH, A-Polymer, H2O2 and FeCl3 | Type | Propeller Mixer
| Diameter | 1250 mm | Tank Water Depth | 1500 mm
| Material (Shaft & Propeller) | SS 316L | Agitator type | Top Entry, Propeller Mixer
| Material (Flange, Nuts & Bolts) | SS 316L | Phase/Voltage | 3/400 V
| Speed of rotation (output) | 50 rpm | Frequency | 50 Hz
| Insulation Class | F | IP | 65
Drawing Number: M-0114, M-0115 & M-0116
LOT 7 – SUPPLY OF SLUDGE SCRAPERS
S.No. | Item Description | Unit | Quantity | OFFERED ITEM MEETS OR EXCEEDS THE SAMPLE TECHNICAL SPECIFICATIONS - Y/N | OFFERED MODEL (exact brand and model name etc.) | Remark (brochure, details, web link)
1 | Supply of primary sedimentation tank sludge Scraper (PSCR 01/01) (Centrally Driven, Diameteral Type with scum removal mechanism), including MS Bridge and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 1
2 | Supply of secondary sedimentation tank sludge Scraper (SSCR 01/01-02) (Centrally Driven, Diameteral Type with scum removal mechanism), including MS Bridge and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 2
3 | Supply of picket fence sludge Scraper (TSCR 01/01) (Centrally Driven Rotating Full-Bridge Type Picket Fence Sludge Scraperwith scum removal mechanism), including MS Bridge and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 1
4 | The Supplier must provide a final report (in English) should be submitted to UNIDO no later than 2 weeks after the delivery and installation of serial number 1 to 3 equipment have been completed. | No | 3
5 | The supplier must carry out trainings of serial number 1 to 3 equipment for the duration as per the requirements of the specific equipment on the installation site of the procure equipment and is aimed at equipping the national expertise with necessary skills and knowledge for maintenance of machines and equipment being procured and operation to produce various building components | No | 2
Technical Specifications (PSCR01)
| Medium | Tannery Wastewater | Type | Centrally Driven, Diameteral TypeScraper
| Tank diameter | 14100 mm | Side Liquid Depth | 3000 mm
| Bed Slope | 1:12 | Free Board (Minimum) | 500 mm
| Central Support Unit Type | Ball type turntable | Material of Fabrication | SS 316L
Technical Specifications (SSCR01)
| Medium | Tannery Wastewater | Type | Centrally Driven, Diameteral TypeScraper
| Tank diameter | 16500 mm | Side Liquid Depth | 3000 mm
| Bed Slope | 1:12 | Free Board (Minimum) | 500 mm
| Central Support Unit Type | Ball type turntable | Material of Fabrication | SS 316L
Technical Specifications (TSCR01)
| Medium | Tannery Wastewater | Type | Centrally Driven Rotating Full-Bridge Type Picket Fence SludgeScraper
| Tank diameter | 15000 mm | Side Liquid Depth | 3000 mm
| Bed Slope | 1:08 | Free Board (Minimum) | 500 mm
| Central Support Unit Type | Ball type turntable | Material of Fabrication | SS 316L
Specifications applied for all scrapers:
- The metal parts of the scrapers system should be made ​​of stainless steel grade SS 316L or better, rectangular and round profiles pipes, plates and leaves. All components must be firmly welded together, and then etched and of course paciolan to provide corrosion protection;
- Framework of circular scraper system construction must be made of hollow profiles of stainless steel SS 316L or better;
- Frame of bridge should match the diameter of the tank and must be resistant to deflection and torsion in relation to the low total weight;
- The bridge must be designed for its own weight, wind loads, load on the steps not less than 200daN.m;
- Work platform and stairs should have protective lattice fence with stainless steel grade SS 316L or better;
- The edge of the grate needs to be bent upwards to form the built leg protection personnel;
- Scum scapers must be made of densely welded hollow profile made of stainless steel SS 316L or better;
- Total weight of scum scapers should be maximally compensated for their buoyancy to minimize loads on the scum scraper wheels;
- Biaxial wheel have to be self-adjusting respectively the radius and the slope of the bottom of the tank. The wheels must be made with pressed onto the rims of the tires of solid rubber, bearings lubricated for life;
- Frame bridge must be secured and rely on a central bearing with elastic intermediate plates compensating inequality track and minimize the deforming force;
- Circular scraper system has a luff movement gear motor, greased for the entire service life that does not require maintenance. The hollow shaft must be made of stainless steel arches of SS 316L or better. Maintenance must be minimized to checking oil level;
- Driving power is transmitted via a free elastic rubber belt to prevent overloading the scraper system and to ensure continued operation in all weather conditions;
- Automatic cleaning of surface by using floating sludge auger conveyor that moves the sludge to built-in surface suction device by their rotation;
- Automatic operation of floating sludge removal system should be provided under conditions of water level fluctuations to 500 mm;
- Control cabinet with contactor switching contacts bepotastine contacts about work and failure must be made of stainless steel. Exterior doors should be transparent and wheather protected window, internal doors should be fitted with one socket for 220 V and one outlet 400 V.
Drawing Number: M-0118 & M-0120
LOT 8 – SUPPLY OF JET AERATION SYSTEM
S.No. | Item Description | Unit | Quantity | OFFERED ITEM MEETS OR EXCEEDS THE SAMPLE TECHNICAL SPECIFICATIONS - Y/N | OFFERED MODEL (exact brand and model name etc.) | Remark (brochure, details, web link)
1 | Supply of Jet Aeration System comprising of jet aerators, air blowers and recirculation pumps for Aeration Tank, including piping and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents.
1.1 | Jet Aerators | No | 2
1.2 | Air Blowers | No | 3
1.3 | Recirculation Pumps | No | 2
2 | The Supplier must provide a final report (in English) should be submitted to UNIDO no later than 2 weeks after the delivery and installation of serial number 1.1 to 1.3 equipment have been completed. | No | 3
3 | The supplier must carry out trainings of serial number 1.1 to 1.3 equipment for the duration as per the requirements of the specific equipment on the installation site of the procure equipment and is aimed at equipping the national expertise with necessary skills and knowledge for maintenance of machines and equipment being procured and operation to produce various building components | No | 3
Technical Specifications (Aeration Tank Dimensions)
| Length | 36000 mm | Width | 24000 mm
| Water Depth | 6000 mm | Depth | 6750 mm
Technical Specifications (Jet Nozzle Assembly)
| Medium | Tannery Wastewater | Type | Jet Aerators with Nozzles
| Bubble Type | Fine bubble | Differential Pressure | 0.7 bar
| Transfer Efficiency | >25 %
Technical Specifications (Air Blowers)
| Type | Positive Displacement Air Blowers | Aeration Capacity | 170 Nm3/min
| Differential Pressure | 0.7 bar
Technical Specifications (Recirculation Pumps)
| Pump Type | Horizontal, Centrifugal, Dry Mounted | Efficiency | >75%
| Pumping Capacity | 870 m3/h (approx.) | Head | 6.0 m
| Phase/Voltage | 3/400 V | Frequency | 50 Hz
Drawing Number: M-0123
LOT 9 – SUPPLY OF SLUDGE PUMPS
S.No. | Item Description | Unit | Quantity | OFFERED ITEM MEETS OR EXCEEDS THE SAMPLE TECHNICAL SPECIFICATIONS - Y/N | OFFERED MODEL (exact brand and model name etc.) | Remark (brochure, details, web link)
1 | Supply of Primary Sludge Pump (PSP01/01-02) in Primary Sludge Pumping Station (PSPS), including pump-motor set, pump base, anchor bolts, pulsation dampers with pressure gauges & pressure sensors (on suction & delivery sides), over pressure and dry run switches, including piping and all other accessories required inside pumping station for installation and operation, complete in all respects, in accordance with the contract documents. | No | 2
2 | Supply of Secondary Sludge Pump (SSP01/01-04) in Secondary Sludge Pumping Station, including pump-motor set, pump base, anchor bolts, pulsation dampers with pressure gauges & pressure sensors (on suction & delivery sides), over pressure and dry run switches, including all piping and other accessories required inside pumping station for installation, complete in all respects, in accordance with the contract documents. | No | 4
3 | Supply of Thickened Sludge Pump (TSP01/01-02) in Thickened Sludge Pumping Station, including pump-motor set, pump base, anchor bolts, pulsation dampers with pressure gauges & pressure sensors (on suction & delivery sides), over pressure and dry run switches, including all piping and other accessories required inside pumping station for installation, complete in all respects, in accordance with the contract documents. | No | 2
4 | The Supplier must provide a final report (in English) should be submitted to UNIDO no later than 2 weeks after the delivery and installation of serial number 1 to 3 equipment have been completed. | No | 3
5 | The supplier must carry out trainings of serial number 1 to 3 equipment for the duration as per the requirements of the specific equipment on the installation site of the procure equipment and is aimed at equipping the national expertise with necessary skills and knowledge for maintenance of machines and equipment being procured and operation to produce various building components | No | 3
Technical Specifications (PSP01)
| Medium | Tannery Wastewater Sludge | Type | Horizontal, Dry Mounted, Screw Centrifugal Impeller
| Capacity | 35 m3/h | Head | 10 m
| Sludge Type | 3% Solid contents | Pump casing | Cast iron (EN-JL 1040, GG25, ASTM A 48 Class 40B)
| Rotor | 1.4301 / 304 SS, Chrome-plated tool steel | Protection | Over Pressure and Dry Run Switch
| Phase/Voltage | 3/400 V | Frequency | 50 Hz
| IP | 65 | Insulation Class | F
Technical Specifications (SSP01)
| Medium | Tannery Wastewater Sludge | Type | Horizontal, Dry Mounted, Screw Centrifugal Impeller
| Capacity | 60 m3/h | Head | 10 m
| Sludge Type | 1-3% Solid contents | Pump casing | Cast iron (EN-JL 1040, GG25, ASTM A 48 Class 40B)
| Rotor | 1.4301 / 304 SS, Chrome-plated tool steel | Protection | Over Pressure and Dry Run Switch
| Phase/Voltage | 3/400 V | Frequency | 50 Hz
| IP | 65 | Insulation Class | F
Technical Specifications (TSP01)
| Medium | Tannery Wastewater Sludge | Type | Horizontal, Dry Mounted, Screw Centrifugal Impeller
| Capacity | 20 m3/h | Head | 10 m
| Sludge Type | 5% Solid contents | Pump casing | Cast iron (EN-JL 1040, GG25, ASTM A 48 Class 40B)
| Rotor | 1.4301 / 304 SS, Chrome-plated tool steel | Protection | Over Pressure and Dry Run Switch
| Phase/Voltage | 3/400 V | Frequency | 50 Hz
| IP | 65 | Insulation Class | F
LOT 10 – SUPPLY OF SLUDGE BELT FILTER PRESS
S.No. | Item Description | Unit | Quantity | OFFERED ITEM MEETS OR EXCEEDS THE SAMPLE TECHNICAL SPECIFICATIONS - Y/N | OFFERED MODEL (exact brand and model name etc.) | Remark (brochure, details, web link)
1 | Supply of Sludge Filter Press (SFP01), including foundation, anchor bolts, painting/coatings and other accessories, with wash water pump, air compressor including anchor bolts, pulsation dampers and other accessories, including piping and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 2
2 | Supply of FRP Container 5 m3(FC01/01-04) for dewatered sludge, including, allaccessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 4
3 | Supply of Ventilation System (VS01) for Sludge Belt Press Room, Watewater Pumping Station, All Sludge Pumping Rooms and Chemical Storage Area, including, allaccessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 6
4 | Supply of Hydrogen Sulphide Detection Equipment (HSD01/01-02) for Sludge Belt Press Room and Coarse Screen Area including, allaccessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 2
5 | The Supplier must provide a final report (in English) should be submitted to UNIDO no later than 2 weeks after the delivery and installation of serial number 1 to 4 equipment have been completed. | No | 4
6 | The supplier must carry out trainings of serial number 1, 3 & 4 equipment for the duration as per the requirements of the specific equipment on the installation site of the procure equipment and is aimed at equipping the national expertise with necessary skills and knowledge for maintenance of machines and equipment being procured and operation to produce various building components | No | 3
Technical Specifications (SP01)
| Medium | Tannery Wastewater Sludge |  | Loading Sludge Rate |  | 20.0 m3/hr
| Input Sludge Concentration | 5% |  | Output Sludge Concentration |  | 15 – 20 %
Technical Specifications (FC01)
| Container Material |  | FRP with vinyl ester resin | Exposed Metal | ANSI Type 316 stainless steel
| Capacity |  | 5 m3 | Protected Metal | ASTM A36, with fiberglass reinforced plastic coating
Technical Specifications (VS01)
| Type |  | Centrifugal Fan with complete ducting | Capacity | 4,000 m3/hr (Air Flow)
| Air Changes |  | 2 air changes/hr in normal conditions | Motor | Phase/Voltage = 3/400 V
4 air changes/hr in emergency conditions
Technical Specifications (HSD01)
| Sensor Type |  | Electrochemical Cell | Measureing Range | 0-500 ppm
| Accuracy |  | ± 2 ppm | Temperature Range | -40 °C to 65 °C
General Specifications:
- Electrical Classifications: Explosion Proof Enclosure
o ATEX: II 2G Ex d IICT6 (Tamb= -34° to +100°C) CSA: Class I, Div 1 & 2, Groups B, C & DC22.2 No 30-M1985 & C22.2 No 142-M1987
- Ingress Protection: NEMA 4X, IP66
- Alarm Relays: Programmable Low and High Alarms, Fault Alarm SPDT Form “C” Relays 2 A @ 250 VAC or 30 VDC
- Accessories: Dust or Splash guard, Flow Adapter with tube fittings, Sensor Duct Mount Kit, Pole Mount brackets.
Drawing Number: M-0117
LOT 11 – SUPPLY OF CHEMICAL DOSING PUMPS
S.No. | Item Description | Unit | Quantity | OFFERED ITEM MEETS OR EXCEEDS THE SAMPLE TECHNICAL SPECIFICATIONS - Y/N | OFFERED MODEL (exact brand and model name etc.) | Remark (brochure, details, web link)
1 | Supply of Chemical Dosing Pumps (DP01) for K-Polymer Dosing Tank, including piping and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 2
2 | Supply of Chemical Dosing Pumps (DP02) for A-Polymer Dosing Tank, including piping and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 2
3 | Supply ofChemical Dosing Pumps (DP03) for Alum Dosing Tank, including piping and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 2
4 | Supply of Chemical Dosing Pumps (DP04) for Hydrogen Peroxide Dosing Tank, including piping and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 2
5 | Supply of Chemical Dosing Pumps (DP05) for Ferric Chloride Dosing Tank, including piping and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 2
6 | Supply of Chemical Dosing Pumps (DP06) for Manganese Sluphate Dosing Tank, including piping and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 2
7 | Supply of Chemical Dosing Pumps (DP07) for Sodium Hydroxide Dosing Tank, including piping and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 2
8 | Supply of Chemical Dosing Pumps (DP08) for Hydrogen Chloride Dosing Tank (02 + 02 standby, one for pH control at Beam House equalization and other at Chemical Oxidation Tank), including piping and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 4
9 | The Supplier must provide a final report (in English) should be submitted to UNIDO no later than 2 weeks after the delivery and installation of serial number 1 to 8 equipment have been completed. | No | 8
10 | The supplier must carry out trainings of serial number 1 equipment for the duration as per the requirements of the specific equipment on the installation site of the procure equipment and is aimed at equipping the national expertise with necessary skills and knowledge for maintenance of machines and equipment being procured and operation to produce various building components | No | 1
Technical Specifications (DP01)
Medium | K-Polymer | Type | Diaphragm with controller
Capacity | 100-300 lit/h | Head | Minimum Head Required
Phase/Voltage | 1/200 V | Frequency | 50 Hz
IP | 65 | Insulation Class | F
Technical Specifications (DP02)
Medium | A-Polymer | Type | Diaphragm with controller
Capacity | 5-15 lit/h | Head | Minimum Head Required
Phase/Voltage | 1/200 V | Frequency | 50 Hz
IP | 65 | Insulation Class | F
Technical Specifications (DP03)
Medium | Alum | Type | Diaphragm with controller
Capacity | 25-100 lit/h | Head | Minimum Head Required
Phase/Voltage | 1/200 V | Frequency | 50 Hz
IP | 65 | Insulation Class | F
Technical Specifications (DP04)
Medium | Hydrogen Peroxide (50%) Solution | Type | Diaphragm with controller
Capacity | 50-120 lit/h | Head | Minimum Head Required
Phase/Voltage | 1/200 V | Frequency | 50 Hz
IP | 65 | Insulation Class | F
Technical Specifications (DP05)
Medium | Ferric Chloride (40%) Solution | Type | Diaphragm with controller
Capacity | 10-25 lit/h | Head | Minimum Head Required
Phase/Voltage | 1/200 V | Frequency | 50 Hz
IP | 65 | Insulation Class | F
Technical Specifications (DP06)
Medium | Manganese Sulphate | Type | Diaphragm with controller
Capacity | 5-50 lit/h | Head | Minimum Head Required
Phase/Voltage | 1/200 V | Frequency | 50 Hz
IP | 65 | Insulation Class | F
Technical Specifications (DP07)
Medium | Sodium Hydroxide | Type | Diaphragm with controller
Capacity | 25-100 lit/h | Head | Minimum Head Required
Phase/Voltage | 1/200 V | Frequency | 50 Hz
IP | 65 | Insulation Class | F
Technical Specifications (DP08)
Medium | Hydrogen Chloride | Type | Diaphragm with controller
Capacity | 25-100 lit/h | Head | Minimum Head Required
Phase/Voltage | 1/200 V | Frequency | 50 Hz
IP | 65 | Insulation Class | F
LOT 12 – SUPPLY OF DISSOLVED OXYGEN, FLOW METER, pH METER AND STANDBY GENERATOR
S.No. | Item Description | Unit | Quantity | OFFERED ITEM MEETS OR EXCEEDS THE SAMPLE TECHNICAL SPECIFICATIONS - Y/N | OFFERED MODEL (exact brand and model name etc.) | Remark (brochure, details, web link)
1 | Supply of Dissolve Oxygen Meter (DO01) for Equalization tank for Beam House and Aeration Tank, including all accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 3
2 | Supply of pH Meter (pH01), including all accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 8
3 | Supply of Wastewater FlowMeters (WFM01/01-02), including all jointing and anchoring material complete in all respects, inaccordancewiththe contract documents
4 | Supply of Sludge Flow Meters (SFM01/01-04), including all jointing and anchoring material complete in all respects, in accordance with the contract documents | No | 4
5 | Supply of Automatic Wastewater Sampler (AS01/01-02), including all jointing and anchoring material complete in all respects, in accordancewiththe contract documents | No | 2
6 | Supply of Standby Diesel Generator (SG01/01) of 750 kVA, including all accessories required for installation and operation, complete in all respects, in accordance with the contract documents. | No | 1
7 | The Supplier must provide a final report (in English) should be submitted to UNIDO no later than 2 weeks after the delivery and installation of serial number 1 to 6 equipment have been completed. | No | 6
8 | The supplier must carry out trainings of serial number 1 to 6 equipment for the duration as per the requirements of the specific equipment on the installation site of the procure equipment and is aimed at equipping the national expertise with necessary skills and knowledge for maintenance of machines and equipment being procured and operation to produce various building components | No | 6
Technical Specifications (DO01)
| Specific Requirements | The aim of dissolved oxygen measurement is to keep the waste treatment process functioning properly and to hold the dissolved oxygen level within an acceptable range and avoid conditions detrimental to the process. The equipment shall be controlled by the PLC system. Meter shall be of the floating ball type. Measurement range 0-10 mg O2/l. Accuracy of ±0.1 on oxygen content. Accuracy on zero ± 0.1 ppm.
| Medium | Tannery Wastewater
Technical Specifications (pH01)
| Specific Requirements | Online pH measurement, range pH 2-12. Accuracy of meter ± pH 0.1.
| Medium | Tannery Wastewater
Technical Specifications (WFM01)
| Specific Requirements | Ultrasonic (Clampable)
| Medium | Tannery Wastewater | Size | DN 100-200
Technical Specifications (SFM01)
| Specific Requirements | Ultrasonic (Clampable)
| Medium | Primary and Secondary Tannery Sludge | Size | DN 100-200
Technical Specifications (SG01)
| Specific Requirements | 600 kW (750kVA) standby rating 380 V D.G Set including skid mounted fuel day tank, 4 pole auto mains failure automatic transfer panel, sound attenuated weather protective enclosure and all control wiring between D.G. Set and Low voltage Switchboard
| Frequency | 50 Hz | Speed | 1,500 rpm
| Compression Ratio | 13:01 | Engine | 4-Stroke Water-Cooled Diesel
Technical Specifications (AS01)
| Specific Requirements | Mobile Automatic Sampler
| Cooling Capacity | w/20 lbs of ice and 4-gal container full | Sampling Modes | Sample Pacing: Uniform time, non-uniform time, flow, flow paced/time switched. Flow pacing is controlled by external flow pulses.
Multiplexing: Samples per bottle: 1 to 50 with 100 ml bottles 1 to 17 with 350 ml bottles Bottles per sample: 1 to 24, multiple bottle compositing.
| Pump | - Adjustable air purge before and after each sample
- Suction tubing allowable length: 1 to 30 m
- Maximum sample lift: 7.9 m
- Pump tubing: recommended life 500,000 pump counts
- Liquid presence detector: Non-wetted, nonconductive sensor detects when liquid sample reaches the pump to automatically compensate for changes in head heights.
LOT 13 – SUPPLY OF PIPES AND FITTINGS
S.No. | Item Description | Unit | Quantity | OFFERED ITEM MEETS OR EXCEEDS THE SAMPLE TECHNICAL SPECIFICATIONS - Y/N | OFFERED MODEL (exact brand and model name etc.) | Remark (brochure, details, web link)
1 | Supply of MS Pipe (Schedule 40) including butterfly valves, tees, elbows, flanged joints, reducers, rubber gaskets, nuts and bolts including fixing the pipe with suitable flat iron strip clamps/bracket, painting etc. complete as required for delivery/suction manifold relating to the pumps, including all accessories required for installation and operation, complete in all respects, in accordance with the contract documents.
| DN150 | RM | 100
| DN 200 | RM | 150
LOT 14 – SUPPLY OF SPARE – PARTS
S.No. | Item Description | Unit | Quantity | OFFERED ITEM MEETS OR EXCEEDS THE SAMPLE TECHNICAL SPECIFICATIONS - Y/N | OFFERED MODEL (exact brand and model name etc.) | Remark (brochure, details, web link)
1 | Supply of Oil & Grease Separator (OGS01/01-02) Waste Oil Submerssible Pump for Beam House and Tan House effluent. | No | 2
2 | Supply of Wastewater Pump (WPS) (WSP01)and (WSP02) in Wastewater Pumping Station (WPS) for Beam House and Tan House respectively. | No | 2
3 | Supply of Submersible Sump Pumps (Bilge Pump SBP01) 1+1 standby in each Wastewater Pumping Station (WPS) and 1+1 standby in each sludge pumping rooms | No | 5
4 | Supply of Jet Aerators Submersible Ejector shaft type (JA01and JA02) in Equalization tank for Beam House and Tan House | No | 2
5 | Supply of Mixer Motor: MRMT1 | No | 1
| Supply of Mixer Motor: MFT01 | No | 1
| Supply of Mixer Motors: MPT01 | No | 2
| Supply of Mixer Motor: MCOT01 | No | 1
| Supply of Mixer Motors: MCDT01 | No | 8
6 | Supply of Jet Aeration System Recirculation Pumps | No | 2
7 | Supply of Jet Aeration System Air Blowers | No | 1
8 | Supply of Primary Sludge Pump PSP01 | No | 1
9 | Supply of Secondary Sludge Pump SSP01 | No | 1
10 | Supply of Thickened Sludge Pump TSP01 | No | 1
11 | Supply of Chemical Dosing Pumps (DP01) for K-Polymer Dosing | No | 1
| Supply of Chemical Dosing Pumps (DP02) for A-Polymer Dosing | No | 1
| Supply ofChemical Dosing Pumps (DP03) for Alum Dosing | No | 1
| Supply of Chemical Dosing Pumps (DP04) for Hydrogen Peroxide Dosing | No | 1
| Supply of Chemical Dosing Pumps (DP05) for Ferric Chloride Dosing | No | 1
| Supply of Chemical Dosing Pumps (DP06) for Manganese Sluphate Dosing | No | 1
| Supply of Chemical Dosing Pumps (DP07) for Sodium Hydroxide Dosing | No | 1
| Supply of Chemical Dosing Pumps (DP08) for Hydrogen Chloride Dosing | No | 1
12 | Supply of Dissolve Oxygen Meter (DO01) | No | 1
13 | Supply of pH Meter (pH01) | No | 1
14 | Supply of Wastewater Flow Meters (WFM01) | No | 1
15 | Supply of Sludge Flow Meters (SFM01) | No | 1
Technical Specifications of All as mentioned from LOT 1 to 13
LOT 15– INSTALLATION AND COMMISSIONING OF EQUIPMENT
S.No. | Item Description | Unit | Quantity | OFFERED ITEM MEETS OR EXCEEDS THE SAMPLE TECHNICAL SPECIFICATIONS - Y/N | OFFERED MODEL (exact brand and model name etc.) | Remark (brochure, details, web link)
1 | Installation, testing & commissioning of Mechanical Coarse Screens (MCS01/01-02) for Beam House effluent, including all accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
2 | Installation, testing & commissioning of Mechanical Coarse Screens (MCS02/01-02) for Tan House effluent, including, all accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
3 | Installation, testing & commissioning of Screen Washer (SW01/01-02) for beam hosue and tan house screenings, including all accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
4 | Installation, testing & commissioning of FRP Container 1.1 m3 (FC03/01-04) for Tan House and Beam House screening, two each respectively, including, all accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 4
5 | Installation, testing & commissioning of Vortex Grit Chamber with Classifier (GC01/01-02) for Beam House effluent, including all piping and other accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
6 | Installation, testing & commissioning of Vortex Grit Chamber with Classifier (GC02/01-02) for Tan House effluent, including, all piping and other accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
7 | Installation, testing & commissioning of FRP Container 5 m3 (FC01/01-05) for Tan House and Beam House wastewater grit, including, all accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 5
8 | Installation, testing & commissioning of Fork Lifter (FL01/01-02) for all type of lifting of containers either chemical or others, including, all accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
9 | Installation, testing & commissioning of Oil & Grease Separator (OGS01/01-02) for Beam House effluent, including all piping and other accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
10 | Installation, testing & commissioning of Oil & Grease Separator (OGS01/01-02) for Tan House effluent, including, all piping and other accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
11 | Installation, testing & commissioning of FRP Container 2 m3 (FC02/01-02) for Tan House and Beam House wastewater waste oil, including, all accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
12 | Installation, testing & commissioning of Wastewater Pump (WPS) (WSP01/01-02) in Wastewater Pumping Station (WPS) for Beam House effluent, including all piping and other accessories required inside pumping station for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
13 | Installation, testing & commissioning of Wastewater Pump (WSP) (WSP02/01-02) in Wastewater Pumping Station (WPS) for Tanning and Post tanning effluent, including, all piping and other accessories required inside pumping station for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
14 | Installation, testing & commissioning of Submersible Sump Pumps (Bilge Pump SBP01/01-08) 1+1 standby in each Wastewater Pumping Station (WPS) and 1+1 standby in each sludge pumping rooms, including pump-motor set, pump base, anchor bolts, painting/coatings and other accessories, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 8
15 | Installation, testing & commissioning of Jet Aerators Submersible Ejector shaft type (JA01/01-02) in Equalization tank for Beam House effluent, including all accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
16 | Installation, testing & commissioning of Aerators Submersible Ejector shaft type (JA02/01-02) in Equalization tank for Tanning & Post Tanning effluent, including, all accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
17 | Installation, testing & commissioning of Mixer (MRMT01/01) for Rapid Mixing Tank, including MS Walkway and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 1
18 | Installation, testing & commissioning of Mixer (MFT01/01) for Flocculation Tank, including MS Walkway and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 1
19 | Installation, testing & commissioning of Mixer (MPT01/01-02) for Pre-Selector Tank, including MS Walkway and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
20 | Installation, testing & commissioning of Mixer (MCOT01/01) for Chemical Oxidation Tank, including MS Walkway and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 1
21 | Installation, testing & commissioning of Mixer (MCDT01/01-04) for Chemical Dosing Tanks, including all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 8
22 | Installation, testing & commissioning of primary sedimentation tank sludge Scraper (PSCR 01/01) (Centrally Driven, Diameteral Type with scum removal mechanism), including MS Bridge and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 1
23 | Installation, testing & commissioning of secondary sedimentation tank sludge Scraper (SSCR 01/01-02) (Centrally Driven, Diameteral Type with scum removal mechanism), including MS Bridge and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
24 | Installation, testing & commissioning of picket fence sludge Scraper (TSCR 01/01) (Centrally Driven Rotating Full-Bridge Type Picket Fence Sludge Scraperwith scum removal mechanism), including MS Bridge and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 1
25 | Installation, testing & commissioning of Jet Aeration System comprising of jet aerators, air blowers and recirculation pumps for Aeration Tank, including piping and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer.
| Jet Aerators | No | 2
| Air Blowers | No | 3
| Recirculation Pumps | No | 2
26 | Installation, testing & commissioning of Primary Sludge Pump (PSP01/01-02) in Primary Sludge Pumping Station (PSPS), including pump-motor set, pump base, anchor bolts, pulsation dampers with pressure gauges & pressure sensors (on suction & delivery sides), over pressure and dry run switches, including piping and all other accessories required inside pumping station for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
27 | Installation, testing & commissioning of Secondary Sludge Pump (SSP01/01-04) in Secondary Sludge Pumping Station, including pump-motor set, pump base, anchor bolts, pulsation dampers with pressure gauges & pressure sensors (on suction & delivery sides), over pressure and dry run switches, including all piping and other accessories required inside pumping station for installation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 4
28 | Installation, testing & commissioning of Thickened Sludge Pump (TSP01/01-02) in Thickened Sludge Pumping Station, including pump-motor set, pump base, anchor bolts, pulsation dampers with pressure gauges & pressure sensors (on suction & delivery sides), over pressure and dry run switches, including all piping and other accessories required inside pumping station for installation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
29 | Installation, testing & commissioning of Sludge Filter Press (SFP01), including foundation, anchor bolts, painting/coatings and other accessories, with wash water pump, air compressor including anchor bolts, pulsation dampers and other accessories, including piping and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
30 | Installation, testing & commissioning of FRP Container 5 m3 (FC01/01-04) for dewatered sludge, including, all accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 4
31 | Installation, testing & commissioning of Ventilation System (VS01) for Sludge Belt Press Room, Watewater Pumping Station, All Sludge Pumping Rooms and Chemical Storage Area, including, all accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 6
32 | Installation, testing & commissioning of Hydrogen Sulphide Detection Equipment (HSD01/01-02) for Sludge Belt Press Room and Coarse Screen Area including, all accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
33 | Installation, testing & commissioning of Chemical Dosing Pumps (DP01) for K-Polymer Dosing Tank, including piping and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
34 | Installation, testing & commissioning of Chemical Dosing Pumps (DP02) for A-Polymer Dosing Tank, including piping and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
35 | Installation, testing & commissioning of Chemical Dosing Pumps (DP03) for Alum Dosing Tank, including piping and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
36 | Installation, testing & commissioning of Chemical Dosing Pumps (DP04) for Hydrogen Peroxide Dosing Tank, including piping and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
37 | Installation, testing & commissioning of Chemical Dosing Pumps (DP05) for Ferric Chloride Dosing Tank, including piping and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
38 | Installation, testing & commissioning of Chemical Dosing Pumps (DP06) for Manganese Sluphate Dosing Tank, including piping and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
39 | Installation, testing & commissioning of Chemical Dosing Pumps (DP07) for Sodium Hydroxide Dosing Tank, including piping and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
40 | Installation, testing & commissioning of Chemical Dosing Pumps (DP08) for Hydrogen Chloride Dosing Tank (02 + 02 standby, one for pH control at Beam House equalization and other at Chemical Oxidation Tank), including piping and all other accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 4
41 | Installation, testing & commissioning of Dissolve Oxygen Meter (DO01) for Equalization tank for Beam House and Aeration Tank, including all accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 3
42 | Installation, testing & commissioning of pH Meter (pH01), including all accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 8
43 | Installation, testing & commissioning of Wastewater Flow Meters (WFM01/01-02), including all jointing and anchoring material complete in all respects, in accordance with the contract documents and as directed by the Engineer. | No | 2
44 | Installation, testing & commissioning of Sludge Flow Meters (SFM01/01-04), including all jointing and anchoring material complete in allrespects, in accordance with the contract documents and as directed by the Engineer. | No | 4
45 | Installation, testing & commissioning of standby diesel generator of 750 kVA, including all jointing and anchoring material complete in allrespects, in accordance with the contract documents and as directed by the Engineer. | No | 2
46 | Installation, testing & commissioning of Automatic Wastewater Sampler (AS01/01-02), including all jointing and anchoring material complete in allrespects, in accordance with the contract documents and as directed by the Engineer. | No | 1
47 | Installation, testing & commissioning of of Gantry Crane (GC01/01) in each Wastewater Pumping Station (WPS) including all accessories, complete in all respects, in accordance with the contract documents and as directed by the Engineer.
48 | Installation, testing & commissioning of MS Pipe (Schedule 40) including butterfly valves, tees, elbows, flanged joints, reducers, rubber gaskets, nuts and bolts including fixing the pipe with suitable flat iron strip clamps/bracket, painting etc. complete as required for delivery/suction manifold relating to the pumps, including all accessories required for installation and operation, complete in all respects, in accordance with the contract documents and as directed by the Engineer.
| DN150 | RM | 100
| DN 200 | RM | 150
LOT 16 – SUPPLY, INSTALLATION AND COMMISSIONING OF LABORATORY EQUIPMENT FOR WASTEWATER ANALYSIS
S.No. | Item Description | Unit | Quantity | OFFERED ITEM MEETS OR EXCEEDS THE SAMPLE TECHNICAL SPECIFICATIONS - Y/N | OFFERED MODEL (exact brand and model name etc.) | Remark (brochure, details, web link)
1 | Supply, installation and commisioning of Analytical Balance (AB01/01), including all accessories required for installation and operation, complete in all respects, in accordance with the provided specifications. | No | 1
2 | Supply, installation and commisioning of Water Distillation Apparatus (Water Still) (WD01/01), including all accessories required for installation and operation, complete in all respects, in accordance with the provided specifications. | No | 1
3 | Supply, installation and commisioning of Thermometer (TH01/02), including all accessories required for installation and operation, complete in all respects, in accordance with the provided specifications. | No | 2
4 | Supply, installation and commisioning of Vacuum Pump (VP01/01), including all accessories required for installation and operation, complete in all respects, in accordance with the provided specifications. | No | 1
5 | Supply, installation and commisioning of Hot Plate Stirrer (Magnetic) (HP01/02), including all accessories required for installation and operation, complete in all respects, in accordance with the provided specifications. | No | 2
6 | Supply, installation and commisioning of Drying Oven (DO01/01), including all accessories required for installation and operation, complete in all respects, in accordance with the provided specifications. | No | 1
7 | Supply, installation and commisioning of pH Meter (Portable) (PH01/02), including all accessories required for installation and operation, complete in all respects, in accordance with the provided specifications. | No | 2
8 | Supply, installation and commisioning of COD Reactor (CD01/01), including all accessories required for installation and operation, complete in all respects, in accordance with the provided specifications. | No | 1
9 | Supply, installation and commisioning of BOD Reactor (BD01/01), including all accessories required for installation and operation, complete in all respects, in accordance with the provided specifications. | No | 1
10 | Supply, installation and commisioning of Incubator (IT01/01), including all accessories required for installation and operation, complete in all respects, in accordance with the provided specifications. | No | 1
11 | Supply, installation and commisioning of Spectrophotometer (Visible) (SPM01/01), including all accessories required for installation and operation, complete in all respects, in accordance with the provided specifications. | No | 1
12 | The Supplier must provide a final report (in English) should be submitted to UNIDO no later than 2 weeks after the delivery and installation of serial number 1 to 11 equipment have been completed. | No | 11
13 | The supplier must carry out trainings of serial number 1 and 11 equipment for the duration as per the requirements of the specific equipment on the installation site of the procure equipment and is aimed at equipping the national expertise with necessary skills and knowledge for maintenance of machines and equipment being procured and operation to produce various building components | No | 1
Technical Specifications (AB01)
Maximum Capacity |  | 220 gm | Readability |  | 0.1 mg
Technical Specifications (WD01)
Capacity |  | 4 Liters/hour | Requirement |  | Distilled Water Production
Technical Specifications (TH01)
Temperature Range | 0 – 250 °C |  |  | Requirement | Sample Temperature Measurement
Technical Specifications (VP01)
Capacity |  | 2.1 m3/h | Requirement |  | Ultimate Vacuum: 70 mbar [Sample Filtration]
Technical Specifications (HP01)
Maximum Plate Temperature |  | 450 °C | Requirement |  | Stirrer Speed: 200 to 1300 RPM
[Sample Heating and Mixing]
Technical Specifications (DO01)
Chamber Capacity |  | 32 Liter | Requirement |  | Max Temperature: 300 °C [Sample Drying]
Technical Specifications (PH01)
Measuring Range: |  | 0.00 – 14.00 | Requirement |  | Resolution: 0.01, Accuracy +0.01, Temperature Range: (–)5 to 105 °C [pH Measurement]
Technical Specifications (CD01)
Capacity |  | 15 Vials (16 x 100 mm) | Requirement |  | Temperature Range: 37 – 165 °C
Timer: 0 – 480 min [Sample Digestion]
Technical Specifications (BD01)
Operating temperature | 5 to 40 ºC | Storage/operating humidity | Maximum relative humidity is 80% for temperatures up to 31 ºC, decreases linearly to 50% relative humidity at 40 ºC
Altitude limit | 2000 m | Range | Selectable, 0 to 35, 0 to 70, 0 to 350, 0 to 700 mg/L, 0 to 1000 mg/L, 0 to 1500 mg/L, 0 to 2000 mg/L,
Pollution degree | 2 | Capacity | Six 492 mL bottles
Technical Specifications (IT01)
Capacity | 260 liters | Requirement | Low temperature Incubator for BOD Range : 0⁰C to 35⁰C
Technical Specifications (SPM01)
Wavelength Range | 320 – 1100 nm | Requirement | COD Measurement
1 | Evaluation of Background of bidder submitting proposal (to be completed) | Compliance Yes/No
1.1 | Local presence in Pakistan and capability to deliver all required services in Pakistan. After sale service either directly by local branch of the bidder, or also authorised agent.
1.2 | Company’s profile and references. Only Bidders with a proven track record and with references in similar projects will be considered. The Bidder should have a proven experience in design and installation of at least three (3) Effluent Treatment Plants with minimum 2,500 m3/day capacity. Bidders should indicate within references – what was their involvement e.g. preparation of the design, construction of similar Effluent Treatment Plants for tanneries, etc. For all references also contacts should be indicated. Company’s profile and references. Only Bidders with a proven track record and with references in similar projects will be considered. The Bidder should have a proven experience in design and installation of at least three (3) Effluent Treatment Plants with minimum 2,500 m3/day capacity. Bidders should indicate within references – what was their involvement e.g. preparation of the design, construction of similar Effluent Treatment Plants for tanneries, etc. For all references also contacts should be indicated.
1.3 | Technical compliance and technically acceptable equipment. Compliance with the specification and standards
1.4 | Technical content and completeness of the proposal as outlined in ToR/TE and all relevant documents, Annexes which are part of the ToR/TE.
1.5 | Compliance with the delivery requirement (INCOTERMs 2010- Delivery Duty Paid (DDP)).
1.6 | Compliance with guarantee/warranty requirements.
1.7 | In its bid the Bidder should confirm that all employees of Bidder and his/her sub-suppliers are treated properly and no discrimination, harassment or other events are present in the Bidder’s organizations.
1.8 | Agreement to the UNIDO contractual terms and conditions.
1.9 | Agreement to the UNIDO Model Contract
1.1 | Agreement to provide Performance Bank guarantee
2 | Evaluation of Technical Aspects of this Contract (to be completed)
2.1 | Understanding of- and adherence to the scope of services to be provided. This will include a management plan, details on quality control / quality assurance measures, material sourcing details, laboratory testing plans, risk management and in-general compliance / management measures to ensure the work is completed as per the Technical Specifications. Drawings and other relevant documents in Annexes.
2.2 | Qualification and experience of proposed key personnel. Complete information should be provided by the bidder, including, full CVs of the proposed team members, a description of the project’s scope and magnitude; details of the bidder’s role and activities during planning, supplying of all items, installation, commissioning, training and other relevant activities.
2.3 | Time schedule for execution of the services: UNIDO will evaluate all information available with respect to the bidder’s ability to develop a project schedule, execute according to that schedule and complete deliverables on time. A bar chart time schedule divided into weeks should be submitted.
2.4 | Bidders’ organization and facilities for accomplishing the requirements: Demonstrated capability to deliver required services in Pakistan. The Bidder should demonstrate presence in Pakistan.
2.5 | Qualification of the sub-contractors – details of subcontractors. Details of the subcontractors, including references of the subcontractor.
2.6 | Safety plan – preparation of site specific safety plan, which outlines measures to protect the site, plant and personnel. At a minimum all workers should be provided with PPE (closed-toe working boots, safety hard hats, gloves, ear / eye protection and visibility clothing / vests). Information and statement of fair treatment and no discrimination, harassment has to be provided (e.g. company policy).
2.7 | SPARE PARTS In the event spare parts are normally delivered with the equipment but are not mentioned in the specifications, please indicate in your Bid the minimum quantity of spare parts required for two (2) years of operations.